## LOG
PO Box 663
1721 HCR 3106
Hillsboro, Texas 76645
Office: 254-582-0205
BobcatContracting.com
Hydrotest Log
Asset Owner: |  | Atmos Energy |  |  | PO/AFE: | 180.6464
Contractor: |  | Bobcat Contracting |  |  | Location: | Henrietta, Tx
Job Number: |  | ATM-4422 |  |  | Date: | 2026-08-29
Deadweights: |  | S/N: | 5496 | Mfg: | Refinery | Calibration Date: |  | 2026-05-08
Pressure Recorder: |  | S/N: | 13045 | Mfg: | Tech-Cal | Calibration Date: |  | 2026-05-08
Ambient Temp: |  | S/N: | 10908 | (L) Mfg: | Tech-Cal | Calibration Date: |  | 2026-05-08
Pipe Temp: |  | S/N: | 10910 | (H) Mfg: | Tech-Cal | Calibration Date: |  | 2026-05-08
Ground Temp: |  | S/N: | 10912 | (M) Mfg: | Tech-Cal | Calibration Date: |  | 2026-05-08
Digital Gauge: |  | S/N: | 021863 | Mfg: | AMETEK | Calibration Date: |  | 2026-05-08
Facility Data
Minimum Test Pressure: |  |  | 4120 | Maximum Test Pressure: |  |  | 4170
Begin GPS: | 33.7132610, -98.1230730 |  |  | Total Footage: |  | 2046
End GPS: | 33.7180270, -98.1248640 |  |  | Test Pump Used/Gallons per stroke |  |  | PDQ - 0.0043
Hydrostatic Test Field Data
Time: | Pressure | Ambient | Pipe | Ground | Comments / Remarks
0.21111 | 0 | 68 | 72 | 84 | Pressure is at 0 psi
0.25069 | 3119 | 68 | 72 | 84 | Reached 75% begin 30 minute hold
0.31458 | 3100 | 64 | 72 | 84 | End 30 minute hold / Begin pressuring up
9:04 | 4158 | 72 | 72 | 84 | Reached test pressure / Begin 15 minute hold
0.39583 | 4160 | 76 | 72 | 83 | Begin 8 hour test
0.40625 | 4167 | 77 | 72 | 82 | Bled down 10 oz 4167-4159
0.41667 | 4162 | 78 | 72 | 82 | Bled down 17 oz 4167-4148
0.42708 | 4148 | 80 | 72 | 82 | Sunny
0.4375 | 4153 | 81 | 72 | 82 | Sunny
0.44792 | 4157 | 82 | 72 | 81 | Sunny
0.45833 | 4162 | 84 | 72 | 81 | Bled down 19oz 4163-4146
0.46875 | 4149 | 86 | 72 | 80 | Sunny
0.47917 | 4153 | 86 | 72 | 80 | Sunny
0.48958 | 4156 | 87 | 72 | 80 | Sunny
0.5 | 4161 | 88 | 72 | 80 | Bled down 16 oz 4161-4146
0.51042 | 4148 | 88 | 72 | 80 | Sunny
0.52083 | 4151 | 89 | 72 | 80 | Sunny
0.53125 | 4158 | 90 | 72 | 80 | Sunny
0.54167 | 4146 | 90 | 72 | 80 | Bled down 13 oz 4158-4147
0.55208 | 4150 | 90 | 72 | 80 | Partly Cloudy
0.5625 | 4153 | 91 | 72 | 80 | Partly Cloudy
0.57292 | 4157 | 92 | 72 | 80 | Partly Cloudy
0.58333 | 4158 | 92 | 72 | 80 | Sunny
0.59375 | 4158 | 98 | 72 | 79 | Sunny
0.60417 | 4156 | 92 | 72 | 79 | Sunny
0.61458 | 4155 | 92 | 72 | 79 | Sunny
Time: | Pressure | Ambient | Pipe | Ground | Comments / Remarks
15:00 | 4153 | 90 | 72 | 79 | Partly Cloudy
0.63542 | 4156 | 92 | 72 | 79 | Partly Cloudy
15:30 | 4157 | 92 | 72 | 79 | Partly Cloudy
0.65625 | 4155 | 90 | 72 | 79 | Sunny
16:00 | 4150 | 92 | 72 | 79 | Sunny
0.67708 | 4146 | 90 | 72 | 80 | Sunny
16:30 | 4145 | 90 | 72 | 80 | Sunny
0.69792 | 4146 | 90 | 72 | 80 | Sunny
17:00 | 4146 | 90 | 72 | 80 | Sunny
0.71875 | 4147 | 92 | 72 | 80 | Sunny
17:30 | 4147 | 91 | 72 | 80 | End of test / Begin 15 min hold
0.73958 | 4146 | 90 | 72 | 80 | End of hold / begin depressurizing line
Bobcat Rep: |  |  |  |  | Date:
Client Rep: |  |  |  |  | Date:

## Summary
PO Box 663
1721 HCR 3106
Hillsboro, Texas 76645
Office: 254-582-0205
BobcatContracting.com
Length: | 2046 | ft
ID: | 4 | In | Location From: |  |  | Location To:
Volume: | 1367 | US Gallon |  | 33.7132610, -98.1230730 |  |  | 33.7180270, -98.1248640
Pipeline Data
O.D. | W.T. | Grade | Length | Buried Pipe | Exposed Pipe | Remarks
4.5" | 0.237" | x42 | 2039' | x | x
4.5" | 0.337" | x52 | 6.5' | x
This is to certify that the system was tested as outlined below:
Type of Test: |  | 8 Hour Hydro Test
Test Medium: |  | Water
Location of Test Unit: |  | 33.71821895882428, -98.124735682387
Maximum Achieved |  | 4167 | pslg | Minumum Achieved |  | 4145 | pslg
The table below indicates the parameters that the pipeline was tested to:
Testing Parameters (Actual)
|  | Pressure | Temperature
|  | pslg | Ambient | Pipe | Ground
Maximum Achieved |  | 4167 | 98 | 72 | 83
Minumum Achieved |  | 4145 | 76 | 72 | 79
Duration of Test, excluding pressurization period
|  | Time | Date | Start Pressure
| From: | 0.39583 | 2026-08-29 | 4160
|  | Time | Date | Final Pressure
| To: | 0.72917 | 2026-08-29 | 4147
Approval: |  |  | Signature |  | Date
Bobcat:
Client:
Inspector:

## Test Stroke Count
Pressure Test Stroke Count
Owner |  | Atmos Energy | [6 empty] | AFE/Auth | 180.6464
Contractor |  | Bobcat Contracting | [6 empty] | Project Name | WL-248
Owner's Rep / Insp |  | Scott Beatty
Service |  | Gas | [6 empty] | Location | Henrietta, Tx
2039' |  |  | 4.5" |  | 0.237" |  | x42 |  | Pack Off Pressure |  |  | 150
6.5' |  |  | 4.5" |  | 0.337" |  | x52 |  | Stabilization Pressure |  |  | 136
[9 empty] | Stroke Count Starts at |  |  | 3100
[9 empty] | Target Test Pressure |  |  | 4160
[9 empty] | Reading Increments |  |  | 10
[9 empty] | Number of Readings |  |  | 106
Begin GPS: | 33.7132610, -98.1230730 |  |  |  | End GPS: | 33.7180270, -98.1248640 |  |  | Pressure Pump Capacity |  |  | 0.0043
Begin GPS: |  |  |  |  | End GPS: |  |  |  | Calculated Incremental Volume |  |  | 0.06076
Begin GPS: |  |  |  |  | End GPS: |  |  |  | Actual Incremental Volume |  |  | 0.08239
Pipeline Fill Field Data
Pressure | Stroke | Difference | Pressure | Stroke | Difference | Pressure | Stroke | Difference | Pressure | Stroke | Difference | Pressure | Stroke | Difference
3100 | 0 | 0 | 3390 | 516 | 19 | 3680 | 1021 | 16 | 3970 | 1709 | 21 |  |  | #N/A
3110 | 10 | 10 | 3400 | 535 | 19 | 3690 | 1037 | 16 | 3980 | 1731 | 22 |  |  | #N/A
3120 | 24 | 14 | 3410 | 554 | 19 | 3700 | 1054 | 17 | 3990 | 1751 | 20 |  |  | #N/A
3130 | 39 | 15 | 3420 | 570 | 16 | 3710 | 1071 | 17 | 4000 | 1772 | 21 |  |  | #N/A
3140 | 56 | 17 | 3430 | 587 | 17 | 3720 | 1100 | 29 | 4010 | 1789 | 17 |  |  | #N/A
3150 | 72 | 16 | 3440 | 605 | 18 | 3730 | 1128 | 28 | 4020 | 1804 | 15 |  |  | #N/A
3160 | 88 | 16 | 3450 | 621 | 16 | 3740 | 1152 | 24 | 4030 | 1814 | 10 |  |  | #N/A
3170 | 106 | 18 | 3460 | 637 | 16 | 3750 | 1178 | 26 | 4040 | 1830 | 16 |  |  | #N/A
3180 | 123 | 17 | 3470 | 654 | 17 | 3760 | 1209 | 31 | 4050 | 1854 | 24 |  |  | #N/A
3190 | 140 | 17 | 3480 | 671 | 17 | 3770 | 1231 | 22 | 4060 | 1865 | 11 |  |  | #N/A
3200 | 158 | 18 | 3490 | 687 | 16 | 3780 | 1266 | 35 | 4070 | 1880 | 15 |  |  | #N/A
3210 | 175 | 17 | 3500 | 707 | 20 | 3790 | 1309 | 43 | 4080 | 1896 | 16 |  |  | #N/A
3220 | 194 | 19 | 3510 | 727 | 20 | 3800 | 1358 | 49 | 4090 | 1911 | 15 |  |  | #N/A
3230 | 212 | 18 | 3520 | 745 | 18 | 3810 | 1379 | 21 | 4100 | 1928 | 17 |  |  | #N/A
3240 | 231 | 19 | 3530 | 763 | 18 | 3820 | 1398 | 19 | 4110 | 1946 | 18 |  |  | #N/A
3250 | 250 | 19 | 3540 | 782 | 19 | 3830 | 1417 | 19 | 4120 | 1966 | 20 |  |  | #N/A
3260 | 268 | 18 | 3550 | 800 | 18 | 3840 | 1438 | 21 | 4130 | 1983 | 17 |  |  | #N/A
3270 | 294 | 26 | 3560 | 821 | 21 | 3850 | 1455 | 17 | 4140 | 1999 | 16 |  |  | #N/A
3280 | 307 | 13 | 3570 | 837 | 16 | 3860 | 1478 | 23 | 4150 | 2014 | 15 |  |  | #N/A
3290 | 327 | 20 | 3580 | 854 | 17 | 3870 | 1499 | 21 | 4160 | 2031 | 17 |  |  | #N/A
3300 | 344 | 17 | 3590 | 871 | 17 | 3880 | 1519 | 20 |  |  | #N/A |  |  | #N/A
3310 | 364 | 20 | 3600 | 888 | 17 | 3890 | 1541 | 22 |  |  | #N/A |  |  | #N/A
3320 | 382 | 18 | 3610 | 904 | 16 | 3900 | 1560 | 19 |  |  | #N/A |  |  | #N/A
3330 | 401 | 19 | 3620 | 921 | 17 | 3910 | 1579 | 19 |  |  | #N/A |  |  | #N/A
3340 | 419 | 18 | 3630 | 938 | 17 | 3920 | 1603 | 24 |  |  | #N/A |  |  | #N/A
3350 | 439 | 20 | 3640 | 954 | 16 | 3930 | 1627 | 24 |  |  | #N/A |  |  | #N/A
3360 | 458 | 19 | 3650 | 972 | 18 | 3940 | 1648 | 21 |  |  | #N/A |  |  | #N/A
3370 | 479 | 21 | 3660 | 987 | 15 | 3950 | 1667 | 19 |  |  | #N/A |  |  | #N/A
3380 | 497 | 18 | 3670 | 1005 | 18 | 3960 | 1688 | 21 |  |  | #N/A |  |  | #N/A
Total Volume Pumped |  |  | 8.7333 |  |  |  | Total Pressure Increase |  | 1060 |  | Double Deviation? Yes or No |  | NO
Actual Incremental Pressure (Total Volume Pumped / Total Pressure Increase X Reading Increments) | [11 empty] | 0.08239
| x | [6 empty] | x
|  | for Owner | [7 empty] | For Bobcat
+/-
+/-
+/-
+/-
+/-
+/-
ft
ft
ft
ft
ft
ft
"OD
"OD
"OD
"OD
"OD
"OD
"wt
"wt
"wt
"wt
"wt
gr
gr
gr
gr
gr
gr
psi
psi
psi
psi
psi
readings
gals/stroke
gals/reading
gals/reading
psi
gals
gals/increme